## Read Me
Soteria Field — LOTO placard export
Generated: 2026-08-29
Placards (active, non-decommissioned equipment): 1
Energy isolation steps: 2
Photos embedded: 2 of 2 referenced
Sheets
Index — every placard page, with a link into the Placards sheet.
Placards — one printable page per placard per language, laid out to match the PDF: title band, equipment bar, warning block, purpose and application process, colour codes, photos, energy-steps table, removal process, signature bar.
Equipment — the loto_equipment row behind each placard, filterable.
Energy Steps — every loto_energy_steps row, filterable.
Summary — per-department counts, computed by formula.
Printing
The Placards sheet is landscape, fit-to-width, with a page break after each placard, so no placard ever shares a sheet with another.
0 of 2 placard pages fit a single Letter sheet; the rest run to 2 sheets. That is the deliberate difference from the PDF: the PDF fits every placard on one page by dropping the isolation-step rows that overflow, and a silently shortened isolation procedure is a safety defect, so this export keeps the full text and takes the extra sheet instead. Machines with the most energy sources are the ones that run long.
Regenerating
python scripts/make_placards.py --data data/ --by-department --out-dir Snak King LOTO Placards by Department
That downloads any missing photos and rebuilds this workbook. It needs no credentials — placard photos are public objects and their URLs are already in the cached equipment.json.

## Index
Equipment ID | Department | Language | Go to placard
SKPK-201 | Main Transfer Fastback | EN | Open
SKPK-201 | Main Transfer Fastback | ES | Open

## Placards
LOCKOUT/TAGOUT PROCEDURE
[EN] Date: 2026-08-29 · Scan for digital placard
EQUIPMENT: SKPK-201 (Main Transfer PC - Main Transfer FB) | [5 empty] | Main Transfer Fastback
KEEP OUT! HAZARDOUS VOLTAGE AND MOVING PARTS
PLACARD-OWNER 2026-05-13: SKPK-MAIN-TRANSFER-FASTBACK covers 13 transfer lanes. Master control. Canonical disconnect on SKPK-205-IP photo.
PURPOSE |  |  |  |  | LOCKOUT APPLICATION PROCESS
This procedure establishes the minimum requirements for lockout of energy-isolating devices. It ensures equipment is stopped, isolated from all potentially hazardous energy sources, and locked out before any servicing or maintenance activities are performed. |  |  |  |  | 1. Communicate to all AFFECTED employees 2. Shut down the equipment using normal stopping procedures 3. Isolate energy sources 4. Apply lockout devices, locks, and tags 5. Release all stored energy 6. Verify equipment is de-energized by attempting to start up 7. After test, place controls in a neutral position
COLOR CODES
E = Electrical | G = Gas |  | H = Hydraulic | P = Pneumatic |  | M = Mechanical |  | T = Thermal
W = Water | S = Steam |  | V = Valve | CG = Compressed Gas |  | CP = Control Panel |  | GR = Gravity
EQUIPMENT IDENTIFICATION AND ENERGY ISOLATION PROCEDURE
PHOTO OF EQUIPMENT |  |  |  | PHOTO OF ISOLATION / DISCONNECT
Energy Tag & Description | Isolation Procedure & Lockout Devices |  |  |  | Method of Verification
E — Electrical ISOLATE ENERGY TAG & DESCRIPTION — E: ELECTRICAL (E) — 208V/480V to FastBack drive motor (often 7.5-15 HP), VFD, controls. 5-minute DC-bus discharge required. | ISOLATION PROCEDURE & LOCKOUT DEVICES — ELECTRICAL: 1. Notify all affected employees that LOTO is being performed on Main Transfer FastBack #1 (SKPK-201). 2. Complete the current cycle and press STOP, then E-STOP. 3. Locate the main electrical disconnect serving this equipment (labeled to the equipment). 4. Open the disconnect to the OFF position. 5. Apply a lockout device through the disconnect handle. Each authorized worker applies their own personal padlock (group-lock hasp if more than one worker) per Cal/OSHA §3314(k). 6. Apply a lockout tag with date, time, name, and reason. 7. If the equipment uses servo drives or VFDs, allow 5 minutes for DC-bus capacitors to discharge before opening any drive enclosure. |  |  |  | METHOD OF VERIFICATION — ELECTRICAL: 1. Use a calibrated voltage tester following the test-before-touch protocol per OSHA 1910.333: test the meter on a known live source, test the disconnect line/load terminals, then re-test the meter on the known live source. 2. Verify zero voltage at the motor or servo terminals downstream of the disconnect. 3. For servo drives / VFDs: confirm DC-bus capacitors have discharged (5-minute minimum) before opening drive enclosure. 4. Attempt to start the equipment from the control panel and HMI — confirm no response. 5. Physically verify all padlocks are secure and lockout tags are legible.
M — Mechanical ISOLATE ENERGY TAG & DESCRIPTION — M: MECHANICAL (M) — Eccentric horizontal-motion drive. ~60 SECOND COAST-DOWN after E-stop — eccentric momentum keeps the deck moving. Do not enter the trough or reach over the deck until full stop verified. | ISOLATION PROCEDURE — MECHANICAL: 1. After electrical isolation per the E procedure, manually verify all rotating/reciprocating components of Main Transfer FastBack #1 (SKPK-201) have completely stopped. 2. Identify residual stored mechanical energy: chain tension, eccentric flywheel/cam momentum, spring-loaded covers and doors. 3. Block, chock, or pin any component that could move under its own weight or stored energy. 4. Where applicable install drive-shaft pins or transmission locks; release belt/chain tension before reaching past the guarding. 5. Apply a lockout tag at the point of mechanical work identifying the worker and the hazard. Cal/OSHA §3314 construes 'minor servicing' narrowly — default to full LOTO including mechanical blocking; do NOT rely solely on the electrical disconnect. |  |  |  | METHOD OF VERIFICATION — MECHANICAL: 1. Visually confirm all rotating and reciprocating components have completely stopped — full coast-down completed. 2. For high-speed servo equipment (case packers, palletizers): wait the manufacturer-specified coast-down before reaching past the guarding. 3. Attempt to manually rotate drive shafts at the input side or jog the system — confirm no movement or kickback. 4. Physically inspect blocks, chocks, or pins for engagement. 5. Confirm belt/chain tension has been released where applicable.
LOCKOUT REMOVAL PROCESS
1. Notify all AFFECTED employees that lockout is being removed 2. Inspect the work area to ensure tools and items have been removed 3. Verify that all employees are clear of the equipment 4. Verify that controls are in the neutral or off position |  |  |  | 5. Remove lockout devices, locks, and tags 6. Re-energize the equipment 7. Notify all AFFECTED employees that the equipment is back in service
Spanish translation on reverse — print double-sided.
Signature |  | Date |  | Dept |  |  | See PM Store in PT Folder
PROCEDIMIENTO DE BLOQUEO/ETIQUETADO
[ES] Fecha: 2026-08-29 · Escanee para placa digital
BORRADOR — NO REVISADO · traducción sin revisar
EQUIPO: SKPK-201 (Main Transfer PC - Main Transfer FB) | [5 empty] | Main Transfer Fastback
¡MANTÉNGASE ALEJADO! VOLTAJE PELIGROSO Y PIEZAS EN MOVIMIENTO
PLACARD-OWNER 2026-05-13: SKPK-MAIN-TRANSFER-FASTBACK covers 13 transfer lanes. Master control. Canonical disconnect on SKPK-205-IP photo.
PROPÓSITO |  |  |  |  | PROCESO DE APLICACIÓN DE BLOQUEO
Este procedimiento establece los requisitos mínimos para el bloqueo de los dispositivos de aislamiento de energía. Garantiza que el equipo se detenga, se aísle de todas las fuentes de energía potencialmente peligrosas y se bloquee antes de realizar actividades de servicio o mantenimiento. |  |  |  |  | 1. Comunicar a todos los empleados AFECTADOS 2. Apagar el equipo usando procedimientos normales de parada 3. Aislar las fuentes de energía 4. Aplicar dispositivos de bloqueo, candados y etiquetas 5. Liberar toda la energía almacenada 6. Verificar que el equipo esté desenergizado intentando arrancarlo 7. Después de la prueba, colocar los controles en posición neutral
CÓDIGOS DE COLOR
E = Eléctrico | G = Gas |  | H = Hidráulico | P = Neumático |  | M = Mecánico |  | T = Térmico
W = Agua | S = Vapor |  | V = Válvula | CG = Gas Comprimido |  | CP = Panel Control |  | GR = Gravedad
IDENTIFICACIÓN DEL EQUIPO Y PROCEDIMIENTO DE AISLAMIENTO DE ENERGÍA
FOTO DEL EQUIPO |  |  |  | FOTO DE AISLAMIENTO / DESCONEXIÓN
Etiqueta y Descripción | Procedimiento de Aislamiento y Dispositivos |  |  |  | Método de Verificación
E — Eléctrico AISLAR ETIQUETA DE ENERGÍA Y DESCRIPCIÓN — E: ELÉCTRICO (E) — 208V/480V al motor FastBack (a menudo 7.5-15 HP), VFD, controles. Se requiere descarga del bus DC de 5 minutos. | PROCEDIMIENTO DE AISLAMIENTO Y DISPOSITIVOS DE BLOQUEO — ELÉCTRICO: 1. Notifique a todos los empleados afectados que se está realizando LOTO en Main Transfer FastBack #1 (SKPK-201). 2. Complete el ciclo actual y presione PARO, luego PARO DE EMERGENCIA. 3. Localice el desconectador eléctrico principal que sirve este equipo (etiquetado al equipo). 4. Abra el desconectador a la posición OFF. 5. Aplique un dispositivo de bloqueo a través de la manija del desconectador. Cada trabajador autorizado aplica su propio candado personal (broche de candado grupal si hay más de un trabajador) per Cal/OSHA §3314(k). 6. Aplique etiqueta de bloqueo con fecha, hora, nombre y razón. 7. Si el equipo usa servo-drives o VFDs, permita 5 minutos para que los capacitores del bus DC se descarguen antes de abrir cualquier gabinete de drive. |  |  |  | MÉTODO DE VERIFICACIÓN — ELÉCTRICO: 1. Use un comprobador de voltaje calibrado siguiendo el protocolo "probar antes de tocar" per OSHA 1910.333: pruebe el medidor en una fuente viva conocida, pruebe los terminales de línea/carga del desconectador, luego re-pruebe el medidor en la fuente viva conocida. 2. Verifique cero voltaje en los terminales del motor o servo aguas abajo del desconectador. 3. Para servo-drives / VFDs: confirme que los capacitores del bus DC se han descargado (5 minutos mínimo) antes de abrir el gabinete del drive. 4. Intente arrancar el equipo desde el panel de control y HMI — confirme que no hay respuesta. 5. Verifique físicamente que todos los candados estén seguros y las etiquetas de bloqueo sean legibles.
M — Mecánico AISLAR ETIQUETA DE ENERGÍA Y DESCRIPCIÓN — M: MECÁNICO (M) — Impulsión horizontal de movimiento excéntrico. ~60 SEGUNDOS DE DESACELERACIÓN después de paro de emergencia — la inercia excéntrica mantiene la cubierta en movimiento. No entre a la artesa ni alcance sobre la cubierta hasta verificar parada completa. | PROCEDIMIENTO DE AISLAMIENTO — MECÁNICO: 1. Después del aislamiento eléctrico per el procedimiento E, verifique manualmente que todos los componentes rotativos/reciprocantes de Main Transfer FastBack #1 (SKPK-201) hayan parado completamente. 2. Identifique energía mecánica almacenada residual: tensión de cadena, inercia excéntrica de volante/leva, cubiertas y puertas accionadas por resorte. 3. Bloquee, calce o pase pasadores a cualquier componente que pudiera moverse por su propio peso o energía almacenada. 4. Donde aplique, instale pasadores en el eje de impulsión o bloqueos de transmisión; libere la tensión de banda/cadena antes de alcanzar más allá del guardado. 5. Aplique etiqueta de bloqueo en el punto de trabajo mecánico identificando al trabajador y al peligro. Cal/OSHA §3314 interpreta la excepción de "servicio menor" en forma estrecha — por defecto LOTO completo incluyendo bloqueo mecánico; NO confíe únicamente en el desconectador eléctrico. |  |  |  | MÉTODO DE VERIFICACIÓN — MECÁNICO: 1. Confirme visualmente que todos los componentes rotativos y reciprocantes han parado por completo — desaceleración completa concluida. 2. Para equipo servo de alta velocidad (empacadoras de cajas, paletizadores): espere la desaceleración especificada por el fabricante antes de alcanzar más allá del guardado. 3. Intente girar manualmente los ejes de impulsión en el lado de entrada o impulsar el sistema — confirme que no hay movimiento ni retroceso. 4. Inspeccione físicamente los bloques, calzas o pasadores en su acoplamiento. 5. Confirme que la tensión de banda/cadena ha sido liberada donde aplique.
PROCESO DE REMOCIÓN DE BLOQUEO
1. Notificar a todos los empleados AFECTADOS que se está retirando el bloqueo 2. Inspeccionar el área de trabajo para asegurar que se hayan retirado herramientas y objetos 3. Verificar que todos los empleados estén lejos del equipo 4. Verificar que los controles estén en posición neutral o apagada |  |  |  | 5. Retirar los dispositivos de bloqueo, candados y etiquetas 6. Volver a energizar el equipo 7. Notificar a los empleados AFECTADOS que el equipo está de vuelta en servicio
Traducción al inglés al reverso — imprimir a doble cara.
Firma |  | Fecha |  | Depto |  |  | Ver PM Store en carpeta PT

## Equipment
equipment_id | description | department | equipment_family | prefix | manufacturer | model | photo_status | has_equip_photo | has_iso_photo | needs_equip_photo | needs_iso_photo | needs_verification | verified | verified_date | verified_by | notes | notes_es | internal_notes | spanish_reviewed | equip_photo_url | iso_photo_url | placard_url | qr_token | readiness_status | last_pre_use_inspection_at | next_periodic_review_due_at | cad_drawing_tag | cad_sheet_ref | cad_grid_ref | facility_floor | flagged_for_review_at | flagged_for_review_by | flagged_for_review_via | flagged_for_review_note | equip_photo_provenance | iso_photo_provenance | iso_photo_is_placeholder | last_audit_verdict | last_audit_at | created_at | updated_at
SKPK-201 | SKPK-201 (Main Transfer PC - Main Transfer FB) | Main Transfer Fastback | general | SKPK |  |  | complete | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE |  |  | PLACARD-OWNER 2026-05-13: SKPK-MAIN-TRANSFER-FASTBACK covers 13 transfer lanes. Master control. Canonical disconnect on SKPK-205-IP photo. |  |  | FALSE | https://zwtnpyjifbdytlektxlc.supabase.co/storage/v1/object/public/loto-photos/SKPK-201-EQ.jpg | https://zwtnpyjifbdytlektxlc.supabase.co/storage/v1/object/public/loto-photos/SKPK-205-IP.jpg |  | b517321040404879 | available | [5 empty] | main |  |  |  |  | field | field | FALSE |  |  | 2026-04-13T19:35:12+00:00 | 2026-06-05T16:57:34.049245+00:00

## Energy Steps
equipment_id | step_number | sequence_order | step_type | energy_type | tryout_required | tag_description | isolation_procedure | method_of_verification | tag_description_es | isolation_procedure_es | method_of_verification_es | confidence
SKPK-201 | 1 | 1 | isolate | E | FALSE | ENERGY TAG & DESCRIPTION — E: ELECTRICAL (E) — 208V/480V to FastBack drive motor (often 7.5-15 HP), VFD, controls. 5-minute DC-bus discharge required. | ISOLATION PROCEDURE & LOCKOUT DEVICES — ELECTRICAL: 1. Notify all affected employees that LOTO is being performed on Main Transfer FastBack #1 (SKPK-201). 2. Complete the current cycle and press STOP, then E-STOP. 3. Locate the main electrical disconnect serving this equipment (labeled to the equipment). 4. Open the disconnect to the OFF position. 5. Apply a lockout device through the disconnect handle. Each authorized worker applies their own personal padlock (group-lock hasp if more than one worker) per Cal/OSHA §3314(k). 6. Apply a lockout tag with date, time, name, and reason. 7. If the equipment uses servo drives or VFDs, allow 5 minutes for DC-bus capacitors to discharge before opening any drive enclosure. | METHOD OF VERIFICATION — ELECTRICAL: 1. Use a calibrated voltage tester following the test-before-touch protocol per OSHA 1910.333: test the meter on a known live source, test the disconnect line/load terminals, then re-test the meter on the known live source. 2. Verify zero voltage at the motor or servo terminals downstream of the disconnect. 3. For servo drives / VFDs: confirm DC-bus capacitors have discharged (5-minute minimum) before opening drive enclosure. 4. Attempt to start the equipment from the control panel and HMI — confirm no response. 5. Physically verify all padlocks are secure and lockout tags are legible. | ETIQUETA DE ENERGÍA Y DESCRIPCIÓN — E: ELÉCTRICO (E) — 208V/480V al motor FastBack (a menudo 7.5-15 HP), VFD, controles. Se requiere descarga del bus DC de 5 minutos. | PROCEDIMIENTO DE AISLAMIENTO Y DISPOSITIVOS DE BLOQUEO — ELÉCTRICO: 1. Notifique a todos los empleados afectados que se está realizando LOTO en Main Transfer FastBack #1 (SKPK-201). 2. Complete el ciclo actual y presione PARO, luego PARO DE EMERGENCIA. 3. Localice el desconectador eléctrico principal que sirve este equipo (etiquetado al equipo). 4. Abra el desconectador a la posición OFF. 5. Aplique un dispositivo de bloqueo a través de la manija del desconectador. Cada trabajador autorizado aplica su propio candado personal (broche de candado grupal si hay más de un trabajador) per Cal/OSHA §3314(k). 6. Aplique etiqueta de bloqueo con fecha, hora, nombre y razón. 7. Si el equipo usa servo-drives o VFDs, permita 5 minutos para que los capacitores del bus DC se descarguen antes de abrir cualquier gabinete de drive. | MÉTODO DE VERIFICACIÓN — ELÉCTRICO: 1. Use un comprobador de voltaje calibrado siguiendo el protocolo "probar antes de tocar" per OSHA 1910.333: pruebe el medidor en una fuente viva conocida, pruebe los terminales de línea/carga del desconectador, luego re-pruebe el medidor en la fuente viva conocida. 2. Verifique cero voltaje en los terminales del motor o servo aguas abajo del desconectador. 3. Para servo-drives / VFDs: confirme que los capacitores del bus DC se han descargado (5 minutos mínimo) antes de abrir el gabinete del drive. 4. Intente arrancar el equipo desde el panel de control y HMI — confirme que no hay respuesta. 5. Verifique físicamente que todos los candados estén seguros y las etiquetas de bloqueo sean legibles.
SKPK-201 | 1 | 1 | isolate | M | FALSE | ENERGY TAG & DESCRIPTION — M: MECHANICAL (M) — Eccentric horizontal-motion drive. ~60 SECOND COAST-DOWN after E-stop — eccentric momentum keeps the deck moving. Do not enter the trough or reach over the deck until full stop verified. | ISOLATION PROCEDURE — MECHANICAL: 1. After electrical isolation per the E procedure, manually verify all rotating/reciprocating components of Main Transfer FastBack #1 (SKPK-201) have completely stopped. 2. Identify residual stored mechanical energy: chain tension, eccentric flywheel/cam momentum, spring-loaded covers and doors. 3. Block, chock, or pin any component that could move under its own weight or stored energy. 4. Where applicable install drive-shaft pins or transmission locks; release belt/chain tension before reaching past the guarding. 5. Apply a lockout tag at the point of mechanical work identifying the worker and the hazard. Cal/OSHA §3314 construes 'minor servicing' narrowly — default to full LOTO including mechanical blocking; do NOT rely solely on the electrical disconnect. | METHOD OF VERIFICATION — MECHANICAL: 1. Visually confirm all rotating and reciprocating components have completely stopped — full coast-down completed. 2. For high-speed servo equipment (case packers, palletizers): wait the manufacturer-specified coast-down before reaching past the guarding. 3. Attempt to manually rotate drive shafts at the input side or jog the system — confirm no movement or kickback. 4. Physically inspect blocks, chocks, or pins for engagement. 5. Confirm belt/chain tension has been released where applicable. | ETIQUETA DE ENERGÍA Y DESCRIPCIÓN — M: MECÁNICO (M) — Impulsión horizontal de movimiento excéntrico. ~60 SEGUNDOS DE DESACELERACIÓN después de paro de emergencia — la inercia excéntrica mantiene la cubierta en movimiento. No entre a la artesa ni alcance sobre la cubierta hasta verificar parada completa. | PROCEDIMIENTO DE AISLAMIENTO — MECÁNICO: 1. Después del aislamiento eléctrico per el procedimiento E, verifique manualmente que todos los componentes rotativos/reciprocantes de Main Transfer FastBack #1 (SKPK-201) hayan parado completamente. 2. Identifique energía mecánica almacenada residual: tensión de cadena, inercia excéntrica de volante/leva, cubiertas y puertas accionadas por resorte. 3. Bloquee, calce o pase pasadores a cualquier componente que pudiera moverse por su propio peso o energía almacenada. 4. Donde aplique, instale pasadores en el eje de impulsión o bloqueos de transmisión; libere la tensión de banda/cadena antes de alcanzar más allá del guardado. 5. Aplique etiqueta de bloqueo en el punto de trabajo mecánico identificando al trabajador y al peligro. Cal/OSHA §3314 interpreta la excepción de "servicio menor" en forma estrecha — por defecto LOTO completo incluyendo bloqueo mecánico; NO confíe únicamente en el desconectador eléctrico. | MÉTODO DE VERIFICACIÓN — MECÁNICO: 1. Confirme visualmente que todos los componentes rotativos y reciprocantes han parado por completo — desaceleración completa concluida. 2. Para equipo servo de alta velocidad (empacadoras de cajas, paletizadores): espere la desaceleración especificada por el fabricante antes de alcanzar más allá del guardado. 3. Intente girar manualmente los ejes de impulsión en el lado de entrada o impulsar el sistema — confirme que no hay movimiento ni retroceso. 4. Inspeccione físicamente los bloques, calzas o pasadores en su acoplamiento. 5. Confirme que la tensión de banda/cadena ha sido liberada donde aplique.

## Summary
Placard export summary
Placards (active equipment) | 1
Energy isolation steps | 2
Rendered placard pages | 2
Department | Placards | Photos complete | Photos partial | Photos missing | Verified
Main Transfer Fastback
Total